## Data
Storage | Pressure_bar | CapCostst_dkg | AnnualCapCostst_dkgyr | StFOM_pct_CAPEX | CapCostComp_dkW | AnnualCapCostComp_dMWyr | CompSpecPower_kWhpkg | CompFOM_pct_CAPEX | Lifetime_yr | mass_stored_kg | Lifetime | WACC | CRF
underground | 100 | 3 | 0.30783 | 0.01 | 1200 | 123133.5917 | 1 | 0.04 | 20 | 1000 | 20 | 0.081 | 0.10261
Note on C2: Author: See Forseberg 2007 based on Chevron Clemens Facility xn storage 2520 metric tonnes of H2
Note on D2: Author: 20 year lifetime
Note on E2: Author: Penev et al. NREL April 2019
Note on H2: Author: Cite Book on H2 storage that quotes 30 to 100 bar pressure ratio number and rounded up to 1 kWh/kg
Note on I2: Author: Penev et al. NREL April 2019

## H2_comp_specpower_costs
H2 pipeline transport
Parameter | Data | Units |  | References/Comments
H2 properties
MW | 2.016 | kg/kmol
LHV | 119.96 | MJ/kg
Cp/Cv | 1.41
1 atm | 101325 | Pa |  |  |  | Assessment of system variations for hydrogen transport by liquid organic hydrogen carriers
73745:15  P0:493
electrolyser;LHV;max
[6 empty] | 73745.15 | -0.493
Compression for storage | [5 empty] | 50 | 10718.6787
Isentropic efficiency | 72% | Assumption
Intercooling temperature | 298 | K
Inlet pressure | 438 | psi | 30 |  |  | 100 | 7616.1145
Outlet pressure | 1460 | psi | 100 | Air liquide US Pipelines |  | 500 | 3444.6195
Number of stages | 2 |  |  |  |  | 1000 | 2447.5607
Pressure ratio at each stage | 1.6667
Wisentropic,each stage | 1364.4347 | kJ/kmol
| 0.6768 | MJ/kg
Wisentropic, total | 1.3536 | MJ/kg
Total electricity requirement | 1.88 | MJ/kg
| 0.52222 | kWh/kg
% of H2 LHV | 1.567%
DOE report estimates for 350 bar refueling: | 2 | kWh/kg | Low | Page 27, section 4.2.2
g | 4 | kWh/kg | High | 1000 kg/d H2 production
System uses 8 or 9 compressors
Costs based on 2007$
Results based on compressing H2 to 875 bar
[6 empty] | H2A distributed production |  | HDSAM Pipeline scenario
[6 empty] | Current | Future | Current | Future
[5 empty] | Compressors | 3 | 1 | 3 | 1
[5 empty] | Isotropic | 65% | 80% | 65% | 80%
[5 empty] | Designed flow rate (each) kg/hr | 63 | 126 | 44 | 89
[5 empty] | Actual shaft power (Each) kW | 177 | 287 | 125 | 203
[5 empty] | Motor rating (each) kW | 208 | 335 | 148 | 238
[5 empty] | kWh/kg | 3.3 | 2.66 | 3.36 | 2.67
[5 empty] | Compressor costs (Each) | 297185 | 259082 | 223169 | 233669
[5 empty] | CAPEX - Each ($/kW) | 1428.774 | 773.3791 | 1507.8986 | 981.8025
[5 empty] | Adjusting for inflation 2007 to 2018 (1.2) | 1714.5288 | 928.0549 | 1809.4784 | 1178.163

## H2 storage_costs_lit
https://www.osti.gov/servlets/purl/1343975
Page 16/54
Cost of vessel (2007 $)
15 | $/kWh H2
500.4167 | $/kg H2
BLS inflation: 2007 to 2017
1.2 | https://www.bls.gov/data/inflation_calculator.htm

## Bulk_H2_StorageCosts
Literature review of capital cost of bulk H2 storage
| 2020-04-29 | [11 empty] | Applies only to Lord et al. (2014) |  |  |  | Applies to Ahluwalia et al. 2019
No. | Reference | Type | Description | Pressure range (bar) | Capacity (tonnes) | Working capacity (%) | Lifetime (years) | Capital cost ($/kg) - no inflation adjustment, reported as in the source | Compression work for loading (kWh/kg) | Cost estimate detail | Notes | Reference | Capital cost ($) - where available | Capital cost of compressor ($) | Capital cost ($) of storage - excluding compressor | Capital cost including compressor ($/kg) | Capital cost of Underground | Capital cost of other (e.g. brine, eng. Contingency) | Capital cost of above-ground ($/kg) | Capital cost of above-ground excluding compressor ($/kg) | Total capital cost including compressor ($/kg)
1 | Eichman et al. (2016) -NREL | Pressure vessel | Storage tanks (generic) | Not provided | 4 or |  | 20 | 1000 | - | Its just an assumption | See page 64/87 | https://www.nrel.gov/docs/fy17osti/67384.pdf
2 | Hydrogen Science and Engineering, Materials, Processes, Systems and Technology (2016) -Edited by Detlef Stolten and Bernd Emonts | Pressure vessel | Spherical vessels | 1.2 | 0.26646 | 1 | NA | 1125.8542 | - | Detailed based on extensive literature review of gas storage and H2 storage literature | See Table 27.9 | https://onlinelibrary.wiley.com/doi/abs/10.1002/9783527674268.ch27
|  | Pressure vessel | Spherical vessels | 2 | 0.46187 | 1 | NA | 874.0184 |  |  |  | https://onlinelibrary.wiley.com/doi/abs/10.1002/9783527674268.ch27
|  | Pressure vessel | Spherical vessels | 2 | 1.5455 | 1 | NA | 725.8797 |  |  |  | https://onlinelibrary.wiley.com/doi/abs/10.1002/9783527674268.ch27
|  |  | Spherical vessels | 2 | 4.6276 | 1 | NA | 548.1132 |  |  |  | https://onlinelibrary.wiley.com/doi/abs/10.1002/9783527674268.ch27
|  | Spherical vessels | Pipe storage (buried underground) | 100 | 64714 | 1 |  | 345.6504 | 0.7 | Cost for a natural gas pipe storage project | Pg 695/1154 and table 27.12; 17 million Euros capex for a project that can store equivalent of 64714 kg (Figure shown below from this reference) | https://onlinelibrary.wiley.com/doi/abs/10.1002/9783527674268.ch27
3 | Ahluwalia et al (2019) - Argonne | Pressure vessel | Pipe storage | <100 bar | 50 | 1 |  | 516 | - |  | Slide 15 - does not include compression costs | https://www.hydrogen.energy.gov/pdfs/review19/st001_ahluwalia_2019_o.pdf
|  | Geological | Salt cavern | 70-190 (120) | 6000 | 0.62 |  | 32.598 | - |  | Slide 17 -Adjusted by excluding compressor capital costs | https://www.hydrogen.energy.gov/pdfs/review19/st001_ahluwalia_2019_o.pdf |  |  |  |  | 17.6 | 8.7 | 9.4 | 3.102 | 35.7
|  | Geological | Underground Lined Rock Cavern | 150 | 672 | 0.95238 |  | 59.942 | 0.7 |  | Slide 19 - adjusted by excluding compressor capex | https://www.hydrogen.energy.gov/pdfs/review19/st001_ahluwalia_2019_o.pdf |  |  |  |  | 46.6 | 15.4 | 9.8 | 11.858 | 71.8
4 | Amos (1998) - NREL | Pressure vessel | Cylindrical tanks | 200 | 10-100 | - |  | 283-503 | 2.2 |  | D.1 (page 104/216) for 454-4536 kg/hr for 1 day - 10-100 tonnes storage | https://www.energy.gov/sites/prod/files/2014/03/f12/25106.pdf
|  | Geological | Salt cavern | 200 |  | - |  | 8.82 | 2.2 |  | D4 (page 116/216) for all flow rates and days of storage | https://www.energy.gov/sites/prod/files/2014/03/f12/25106.pdf
5 | Lord et al. (2014) | Geological | Salt cavern | ~100 | 2486 | 0.76911 |  | 18.6794 | 2.2 |  | Total capital cost includes compressor capital costs | https://www.sciencedirect.com/science/article/abs/pii/S0360319914021223 | 63254547 | 27539480 | 35715067 | 33.0829
|  | Geological | Depleted Oil & gas reservoir | ~100 | 2868 | 0.66667 |  | 11.3741 | 2.2 |  | Total capital cost includes compressor capital costs | https://www.sciencedirect.com/science/article/abs/pii/S0360319914021223 | 40106938 | 18359654 | 21747284 | 20.9764
|  | Geological | Hard rock | ~100 | 2486 | 0.76911 |  | 32.4815 | 2.2 |  | Total capital cost includes compressor capital costs | https://www.sciencedirect.com/science/article/abs/pii/S0360319914021223 | 89644020 | 27539480 | 62104540 | 46.8849
|  | Geological | Aquifer | ~100 | 2868 | 0.66667 |  | 11.8409 | 2.2 |  | Total capital cost includes compressor capital costs | https://www.sciencedirect.com/science/article/abs/pii/S0360319914021223 | 40999458 | 18359654 | 22639804 | 21.4432
6 | Forseberg et al. (2006) | Geological | Salt cavern | ~100,000 | 2520 |  |  | 0.8-1.6 | - |  | Based on ConocoPhillips Clemens Terminal in Texas | http://citeseerx.ist.psu.edu/viewdoc/download?doi=10.1.1.133.9925&rep=rep1&type=pdf
Background information
|  | STP definition | 100 | kPa
|  | Pressure | 0 | Deg C
|  | Temperature | 0.002016 | g/mol
MW H2
|  | Mass of 1 m3 at STP | 0.088821 | kg
|  | 1 USD | 0.76 | Euro